## Checklist
Rectangular Duct Transverse Joint Sealing Inspection (Pre-Insulation) Guide
Completed by: |  |  | Date:
See Instructions for guidance. Record results and notes in the shaded cells.
No. | Section | Check / Requirement | Result | Notes / Evidence
1 | Record joint ID and location | Record the joint identifier, duct run, and exact location on the plan or tag.
2 | Photograph joint from all sides | Take clear photos of the joint from all four sides before touching anything.
3 | Verify surfaces clean and dry | Confirm areas around the joint are clean, dry, and free of oil, dust, or loose debris.
4 | Check flange alignment and contact | Verify mating flanges are even and fully seated with no visible steps or gaps around the perimeter.
5 | Confirm gasket installed (if used) | If this joint type uses a flange gasket, verify a continuous gasket is present and properly seated between flanges.
6 | Check gasket compression | Inspect for uniform gasket compression; no visible daylight along the flange-to-flange seam.
7 | Verify continuous exterior seal | Confirm a continuous seal exists around the entire perimeter at both the flange-to-flange seam and the flange-to-duct edge.
8 | Inspect corner pieces seated | Check each flange corner piece is fully seated and properly installed.
9 | Verify corner sealing complete | Confirm sealant is applied at all four corners with no gaps or pinholes.
10 | Verify bolt/rod penetrations sealed | Confirm all bolt or rod penetrations (including washers) have visible exterior sealing.
11 | Check nearby penetrations sealed | Verify any screw holes or accessory penetrations near the joint are sealed on the exterior.
12 | Hand-check fastener tightness | Attempt to turn several nuts/bolts by hand on each side; any that turn freely require tightening before resealing if disturbed.
13 | Check tape adhesion (if used) | If tape is used, verify full adhesion with edges firmly rolled and no lifting or loose ends.
14 | Check reinforcing mesh (if used) | If reinforcing mesh is used with mastic, confirm mesh is fully embedded and not exposed.
15 | Probe for adhesion and lifting | Lightly probe sealant or tape; confirm no lifting, peeling, or loose sections.
16 | Scan for defects | Visually scan for pinholes, voids, wrinkles, or fishmouths and mark any defects for rework.
17 | Inspect hidden/backside areas | Use a flashlight and mirror to inspect hidden and backside flange areas.
18 | Check behind hangers/supports | Verify no sections behind hangers or supports are left unsealed.
19 | Confirm exterior perimeter complete | Confirm no unsealed seams or holes remain anywhere on the joint’s exterior perimeter.
20 | Remove excess sealant | Confirm no excess sealant is hanging, dripping, or likely to detach; clean up as needed.
21 | Check sealant is dry-to-touch | Touch sealant in a discreet spot; surface should be dry-to-touch (tack-free) before insulating.
22 | Record results and rework | Document pass/fail, noted defects, and required rework with date, time, initials, and attach photos.

## Instructions
Rectangular Duct Transverse Joint Sealing Inspection (Pre-Insulation) Guide
Before insulation hides the work, verify each rectangular duct transverse joint is clean, aligned, sealed continuously, and dry-to-touch. This prevents air leakage, reduces rework, and protects system performance.
Record the joint ID, duct run, and exact location; photograph the joint from all four sides before touching anything.
Verify surfaces are clean and dry; check flange alignment and that any gasket used is present and uniformly compressed with no daylight.
Confirm a continuous exterior seal around the entire perimeter at both the flange-to-flange seam and flange-to-duct edge; ensure corners are seated and sealed.
Verify all bolt/rod penetrations (including washers) and any nearby screw holes or accessories are sealed on the exterior.
If tape is used, check adhesion and rolled edges; if mesh with mastic is used, confirm it is fully embedded; lightly probe to ensure no lifting or loose sections.
Hand-check several nuts/bolts per side; tighten any that turn freely and reseal if disturbed; remove excess sealant and clean up.
Use a flashlight and mirror to inspect hidden/backside areas and behind hangers; confirm no unsealed seams remain and that sealant is dry-to-touch; document results and any rework.
Record Done, Not done or N/A. Use Notes / Evidence for observations and follow-up.
Project / Location: ____________________