## Sheet1
Generated file by QChecklists
https://quollnet.com/checklist
Test façade condensation risk zones, project conditions
Test façade condensation risk zones under project operating conditions with an interactive checklist that is commentable and export as PDF/Excel. Reliable QA.
Project:
| Filled by: |  | Date:
Pre-Test Planning
1 | Confirm test scope, elevations, and interior zones per latest drawings; acceptance: complete location matrix with gridlines/room IDs; evidence: approved test plan with signatures and date stamp.
2 | Verify operating conditions align with project setpoints and occupancy; method: review BMS trend logs (24 h); acceptance: within setpoint ±2 °C, RH 40–60%; evidence: screenshots.
3 | Identify likely thermal bridges (mullions, slab edges, anchors) using shop drawings; acceptance: prioritized inspection list; evidence: annotated details highlighting high-risk nodes.
4 | Secure permits and access per approved project specifications and authority requirements; acceptance: permits valid for test window; evidence: uploaded approvals and toolbox talk attendance.
Instrument Calibration and Setup
5 | Calibrate infrared camera with reference source; set emissivity per material (e.g., painted gypsum 0.90±0.02); acceptance: calibration certificate current; evidence: photo of settings and serial.
6 | Verify surface temperature probe using ice-water bath (0 °C ±0.3 °C); acceptance: deviation ≤0.3 K; evidence: photo of reading and log entry.
7 | Deploy indoor RH/T data loggers at 1.1 m height, ≥0.5 m from façades; acceptance: accuracy ±2% RH, ±0.3 °C; evidence: placement photos with IDs.
8 | Configure logger interval 1–5 min and synchronize device clocks; acceptance: timestamps within ±1 min across devices; evidence: time sync screenshot.
9 | Set up shaded outdoor RH/T sensor at 1.5–2.0 m and anemometer; acceptance: secure mounting, no direct sun or rain; evidence: location photo with GPS tag.
10 | Confirm IR camera spot size ratio suits distance; acceptance: pixel footprint ≤10 mm at target; evidence: distance note and lens spec.
On-Site Environmental Stabilization
11 | Maintain HVAC setpoints (e.g., 21 ±2 °C; 40–60% RH) for ≥4 h pre-test; acceptance: drift ≤±0.5 K and ±2% RH in last hour; evidence: BMS/logger trends.
12 | Confirm indoor–outdoor temperature difference ≥10 K for thermography; if <10 K, plan contact probe emphasis or reschedule; evidence: contemporaneous indoor/outdoor readings.
13 | Shut operable windows/vents and typical internal doors as per operations; acceptance: steady-state airflow documented; evidence: photos and note of deviations.
14 | Avoid direct solar gain or wet façades; defer sunlit/rain-affected elevations for ≥24 h drying; evidence: weather log and façade condition photos.
Measurement and Mapping
15 | Log indoor RH/T every 5 min throughout testing; acceptance: drift ≤±2% RH and ±0.5 K; evidence: exported CSV and logger screenshots.
16 | Measure interior surface temperatures at corners, slab edges, and mullions on 1 m grid; acceptance: ≥5 points per bay; evidence: point list with coordinates.
17 | Capture paired visual and IR images per façade bay; include spot and isotherm overlays; acceptance: focus and scale marker visible; evidence: image IDs tied to locations.
18 | Check air leakage at joints using smoke pencil under normal operation; acceptance: no sustained inward smoke stream; evidence: short video clip and notes.
19 | Scan glazing edges and spandrels for cold stripes; acceptance: anomalous ΔT patterns documented; evidence: IR thermograms with temperature scale bar.
20 | Measure surface moisture with pinless meter at suspect zones; acceptance: ≤15% wood-equivalent or within material baseline; evidence: readings and photos.
21 | Record any visible condensation, fogging, or dripping and timestamp; acceptance: correlate with RH/T at that minute; evidence: photos and event note.
Analysis and Reporting
22 | Compute indoor dew point from RH/T and compare to surface temperatures; acceptance: surface temp ≥ dew point + 2 K; evidence: calc sheet and screenshots.
23 | Calculate surface temperature factor fRsi=(Tsi−Te)/(Ti−Te) at cold spots; acceptance: meets specified threshold (target ≥0.75 if unspecified); evidence: table with inputs.
24 | Map risk zones on elevation drawings with severity codes and actions; acceptance: every bay classified and signed off; evidence: annotated PDF and action log.
Comments
Filled by:
Signature:
Introduction |  |  | How to use this checklist
Test façade condensation risk zones under project operating conditions ensures your building envelope performs safely during real HVAC setpoints, occupancy, and weather. This in-situ façade condensation assessment blends thermal imaging, surface temperature testing, and hygrothermal analysis to locate and rank dew-prone areas before damage occurs. The checklist focuses on interior-facing façade elements only: glazing, frames, spandrels, slab edges, and junctions. It excludes roof assemblies, below-grade walls, and laboratory-only methods. By controlling environmental variables and capturing defensible evidence, you prevent mold growth, finishes deterioration, and warranty disputes. You will learn how to stabilize conditions, select instruments, capture RH/temperature data, compute dew point margins, and map risk zones clearly on drawings. The outcome is a repeatable method that ties measured surface temperatures and indoor psychrometrics to actionable pass/fail criteria, per approved project specifications and authority requirements. Use this interactive checklist now: tick items, add comments, and export PDF/Excel with a secure QR for sign-off. |  |  | 1. Preparation: Gather IR camera, calibrated surface probes, RH/T loggers, smoke pencil, moisture meter, tripod, and PPE. Coordinate access, confirm HVAC setpoints, and review drawings to prioritize high-risk façade zones. 2. Verify Conditions: Confirm indoor–outdoor ΔT, stabilize RH/temperature, and check for sun or rain on façades. Synchronize device clocks and set logging intervals before starting measurements. 3. Start Interactive Mode: Open the checklist, tick each step as completed, and attach photos, readings, and documents to the relevant item. Use comments to record deviations and approvals. 4. Record Measurements: Log RH/T, capture paired IR and visual images, take contact surface readings, and map locations by gridline/room ID. Note observed condensation or air leakage with timestamps. 5. Analyze and Export: Calculate dew point margins and fRsi, classify risk zones, and generate the summary. Export the full, commentable report as PDF/Excel directly from the checklist. 6. Sign-Off: Collect digital signatures from contractor, QA, and client. Distribute the QR-authenticated package and archive raw data, calibration records, and annotated drawings for traceability.